## Slide 1: 博 克 聯 合 有 限 公 司 PULTEK ASSOCIATION CO.,LTD
Established : 1998/ 9 月
Capital : USD 300,000.
Head Office : Hsin chu , Taiwan ,R.O.C
Revenue： NTD 6000 萬
Affiliated company：
盛郁實業有限公司
Primary-Tech-Enterprise Co.,LTD
勝益氣體股份有限公司
Shen Yi Gas Co.,LTD
Main Business :
Instrumentation Fittings & Valves
GAS MFM & MFC
BA/EP SUS 316L Tube
Tube Welding Fitting

## Slide 2: 博 克 聯 合 有 限 公 司 PULTEK ASSOCIATION CO.,LTD
 | Fitting Industry Valve UCV Valve |  | UCV Valve Bellow Valve
 | Replace Brand ：Swagelok |  | Replace Brand ：Fujikin
 | conversion ratio：90% |  | conversion ratio：70%
 | Digital MFM & MFC Analog MFM & MFC Heavy Idustry Thermal MFM Mass Vortex Flow Meter |  | UHP Regulator UHP Valve Vaccum Generator Module Flow Switch
 | Replace Brand ：MKS , Horiba , Fufikin |  | Replace Brand ：Parker
 | conversion ratio：80% |  | conversion ratio：90%
 | Metal Gas Filter Metal Gasket Filter Flow Restrictors Metal Difuuser |  | Pressure Gauge Pressure Transmitter
 | Replace Brand ：PALL , TEM |  | Replace Brand : Nagano
 | conversion ratio：60% |  | conversion ratio：90%

## Slide 3
Definition of regulator parts
Regulator Function
Regulator types
Regulator Leak
Regulator Introduction

## Slide 4
Regulator Parts

## Slide 5
Body
--Materials
  316 L double melt
  316 L single melt
  Hastelloy
Poppet Spring
--Materials
  316 SST single melt
  Hastelloy
Regulator Parts

## Slide 6
Poppet
--Meters gas across seat
--Moves vertically down
away from seat
Seat
--Forms the orifice in the
regulator
--Materials
  PCTFE
  Vespel
  Peek
Regulator Parts

## Slide 7
Nozzle
--Clamps seat in the body
Diaphragm
-- Materials
Ni-Cr-Mo alloy
--Normally incorporates
convolutions to provide
better diaphragm movement
Regulator Parts

## Slide 8
Cap Assembly
--adjusting stem and spring
on diaphragm to set outlet
pressure
Bonnet Nut
--Holds cap assemble and
diaphragm against body of
regulator
Regulator Parts

## Slide 9: (How It Works)
Regulators are used to reduce an inlet pressure to a lower outlet pressure
If on/off shut off is desired, use a valve not a regulator
Regulator Function

## Slide 10
No gas introduced, so no pressure
Knob turned off
--Poppet closed against seat
--Gas contained to inlet side
Turning knob
--compresses spring creating downward force on diaphragm
--Poppet pushed away from seat allowing gas to flow from inlet side to outlet side
Regulator Function

## Slide 11: Outlet Pressure Setting Achieved
Knob Spring downward force on diaphragm
Gas pressure creates upward force on diaphragm
Set point achieved when forces are equal
At set point, with no flow, poppet is against the seat
Regulator Function

## Slide 12: Pressure Drop with Flow
Static Condition
  *Flow: 0 SLPM
*5 SLPM Flow Rate
-- Outlet pressure decreases
from 30 psig to 29 psig
*10 SLPM Flow Rate
-- Outlet pressure falls
from 29 to 24 psig
Regulator Function

## Slide 13: Droop Causes and Effects
Adjustment spring extension
Supply pressure & pressure fouce area
  --Force required to move
  diaphragm and poppet
  away from seat
  -- Supply pressure
  --Orifice (annular area
  between seat and poppet)
  and diaphragm effective
  area and stroke (travel)
Force balance equation:
Adjustment Spring=Supply pressure+pressure fouce area
Regulator Function

## Slide 14: Droop Chart/Curve
AP1500 flow curves with four different inlet pressures
Vertical axis for pressure and horizontal axis flow
As inlet pressure decreases, droop increases
Regulator Function

## Slide 15: Supply Pressure Effect
Regulator shown attached to full gas cylinder at 2200 psig
Gas cylinder is consumed to 200 psig
Note outlet pressure rise to 40 psig Flow
Flow rate still constant at 1 SLPM
Regulator Function

## Slide 16: Supply Pressure Effect - Cause
**Supply pressure effect
determined by ratio of
diaphragm area to
orifice area
Force balance equation
--A = B + C
Gas cylinder from 2200 to 200 psig
-- “C” decreases
Force “B” increases
--maintain the force balance
Regulator Function

## Slide 17: Examples
low flow regulator
--0.5 psi rise per 100 psi drop in source pressure
--10 psi rise in outlet for a 2,000 psi drop in source pressure
high flow regulator
--4 psi rise per 100 psi drop in source pressure
-- 80 psi rise in outlet for a 2,000 psi drop in source pressure
Regulator Function

## Slide 18
Free Poppet Regulators
Tied Diaphragm Regulators
Two Stage Regulators
Absolute Pressure Regulators
Springless Regulator
Regulator Types

## Slide 19: Free Poppet Regulator
Not have a mechanical link between the diaphragm and poppet
If particle are in the gas they can get lodged between the seat and the poppet
gas leaks across the seat causing an increase of outlet pressure
Pressure rises to over 80 psig
Regulator Types

## Slide 20: Tied Diaphragm Regulator
Mechanical link between the diaphragm and poppet
Particle again shown coming through gas stream and lodging between seat and poppet
gas leaks across the seat causing an increase of outlet pressure
The link between poppet and diaphragm,diaphragm pulls poppet tighter
Regulator Types

## Slide 21: Two Stage Tied Diaphragm Regulator
Two stage regulators are simply two regulators in series in a common body
Cylinder pressure decays, 1” stage outlet pressure rise is small and doesn’t cause change in 2” stage outlet pressure
Note: pressure and flow conditions
Regulator Types

## Slide 22: Absolute Pressure Regulators
Designed to deliver outlet pressures below atmospheric pressure (vacuum)
Incorporate a bias spring pushing or pulling the diaphragm to allow vacuum to be controlled on the outlet side
Regulator Types
Notes: Instructor Notes:
Cover structural differences – reverse bias spring. Location and function.

## Slide 23: Springless Regulator
Springless means no poppet spring
Mechanism to attach poppet expensive
No difference in performance, meaning particle generation, dry down or regulation
Increased cost with no benefit
Diaphragm is still a wetted spring
Regulator Types

## Slide 24: Across the Seat Leak
Leakage is caused by particles lodging between the seat and the poppet
These particle prevent the poppet from fully closing and allow gas to leak across the seat
Generally caused by contaminates from the cylinder or poor purge technique
Regulator abnormal

## Slide 25: Across the seat leak causes
Contamination from the gas source, either particles or moisture
Contamination from the piping system, such as tubing facing chips
Contamination created by poor purging technique or allowing moisture into piping
Wrong seat material for gas
Exceeding the temperature rating of the device
Regulator abnormal

## Slide 26: Outboard Leak
Outboard leakage is leakage from inside the regulator to the atmosphere
Though very rare, most common leak path is at body to diaphragm seal
Regulator abnormal

## Slide 27: Outboard leak (continued)
A leak detected at the bonnet nut leak check port is a diaphragm to body seal leak
A leak detected through the bonnet vent port is a leak through the central region of the diaphragm
Regulator abnormal

## Slide 28: Outboard leak main causes
Excessive cycle purging can cause a diaphragm fracture when diaphragm cycle life, vacuum to positive pressure cycles, is exceeded
Over pressurization of the diaphragm can cause diaphragm to body leak or fracture
Corrosion on diaphragm, either internal or external, can cause diaphragm leak
Regulator abnormal

## Slide 29: Operator induced failure
Wrong regulator selection for application
  Materials of construction not compatible
  Sized improperly for flow or pressure
Pressure lock up with tied diaphragm regulator
  Closed regulator with trapped pressure under the diaphragm pulling poppet into seat
Regulator abnormal

## Slide 30: Regulator Selection
Review of type Information
Free-Poppet
- No Mechanical Linkage
between poppet and Dia.
Tied-Diaphragm
- Mechanical Linkage
between poppet and Dia.
Tow-Stage
- 2 Single Stage combine
Absolute Regulator
- Can be regulated by pressure
100 mg absolute~10 Psi

## Slide 31: Regulator Selection

## Slide 32: Regulator Selection
Example: SiH4 , Source Regulator , 120 lpm , Inlet:1400Psi Out:100 Psi |  |  | 
Type | Free poppet |  | 
 | Tied-Diaphragm |  | 
Gas | Corrosive | Double Melt Hastelloy | 
 | Non-Corrosive | SS316L | 
Flow | 0~120SLPM | Standard | 
 | 120~600SLPM | Intermediate | 
 | 800~1500 SLPM | High Flow | 
Other | 2Port , 3Port , 4Port |  | 

## Slide 33: Regulator Selection

## Slide 34: Regulator Selection

## Slide 35: Q A Time
Questions and answers